GCC Automation Scripts

User manual — FRT and frequency studies in PowerFactory

Scripts: gcc_frt_script 5.0 · gcc_freq_script 3.0 · gcc_export_results 1.3 / Rev2 2.1 · gcc_common 2.0

# 1. What the scripts do

The scripts automate grid code compliance (GCC) simulation studies in DIgSILENT PowerFactory. From two YAML files — a project config and a grid code file — they build every required study case, run the RMS simulations and export the results to CSV for evaluation.

The workflow has three steps:

- Configure — enter plant data and PowerFactory element names in project_config_update.yaml and point it at the grid code file.

- Simulate — run gcc_frt_script.py (fault ride-through) and/or gcc_freq_script.py (FSM, LFSM-O, LFSM-U). Each creates a timestamped run folder of study cases and writes a JSON run manifest.

- Export — run gcc_export_results.py to write one CSV file per study case plus an export manifest.

| File | Role |
| --- | --- |
| project_config_update.yaml | Project, plant, element names, output folder and simulation settings. The only file you edit per project. |
| netherlands_NC-RfG-TypeD.yaml | Grid code requirements: fault types, retained voltage levels, clearance times, frequency step sequences. |
| gcc_frt_script.py | Creates and runs the FRT cases: fault type × retained voltage × Q0/Qmax/Qmin (45 cases for NL Type D). |
| gcc_freq_script.py | Creates and runs a Ramp and a Step case for each applicable frequency mode (6 cases for NL Type D). |
| gcc_export_results.py | Exports each case to CSV with fixed, named columns. Reads the project config and run manifest. |
| gcc_export_results_Rev2.py | Alternative exporter: needs no config, exports every recorded variable with “element ¦ variable” headers. |
| gcc_common.py | Shared library imported by all scripts. Not run directly. |

# 2. One-time setup

## 2.1 Install PyYAML

The scripts read YAML files, so PowerFactory's Python needs PyYAML. Run once from a command prompt (adjust the path to your PowerFactory version), then restart PowerFactory:

"C:\Program Files\DIgSILENT\PowerFactory 2025 SP4\Python\3.13\python.exe" -m pip install pyyaml

## 2.2 Keep the files together

Keep all .py files in one folder (e.g. ...\Codemasters\Working Scripts\). Every script imports gcc_common.py from its own folder, so they must stay side by side.

## 2.3 Create the ComPython objects

In PowerFactory, create one ComPython (Python script) object per script you will run and point its script file at the .py file:

- gcc_frt_script.py

- gcc_freq_script.py

- gcc_export_results.py (or gcc_export_results_Rev2.py)

## 2.4 Point the scripts at your config

Near the top of gcc_frt_script.py, gcc_freq_script.py and gcc_export_results.py, set CONFIG_FILE to your project config. It can be a file, a folder containing project_config.yaml or project_config_update.yaml, or None to use project_config.yaml next to the script.

CONFIG_FILE = r"C:\Projects\GCC Script Development\Codemasters\Working Scripts\project_config_update.yaml"

## 2.5 Prepare the PowerFactory project

- A base study case named GCC_BaseCase (or the name in elements.base_case) in the Study Cases folder. Every case is a copy of it.

- The base case contains a Simulation Events/Fault event folder. Keep it free of short-circuit events — the FRT script adds the fault and clearing events itself.

- For frequency studies: an AC voltage source (ElmVac) that sets the grid frequency, named in elements.freq_voltage_source. The Ramp cases use the frequency ramp events already present in the base case (loaded from an external .txt file); the Step cases add their own step events. Because both are copies of the same base case, check that the Step cases do not also contain the ramp events.

- A station controller (ElmStactrl), a power-frequency controller (ElmSecctrl) and an external grid (ElmXnet). The scripts set their control modes and setpoints per case.

# 3. Configure a project

Edit project_config_update.yaml. The sections are:

| Section | What to enter |
| --- | --- |
| project | Name, number, client, country, author, date. Copied into the manifests. |
| plant | pmax_mw, poc_voltage_kv, q_factor (Qmax = +q_factor × Pmax, Qmin = −q_factor × Pmax), plant_type (type_1 synchronous / type_2 converter-based — selects which requirement block of the grid code is used), technology, module_type. |
| grid_code | file: path to the grid code YAML. A relative path is resolved against the config file's folder. |
| elements | The exact PowerFactory loc_name of each model element (table below) and base_case. |
| results | output_dir: where run manifests and exported CSVs are written. |
| simulation | Run flags and FRT timing (section 4.1). |

| Element key | PF class | Used by |
| --- | --- | --- |
| poc_busbar | ElmTerm | FRT, FREQ, export — faults applied here; POC voltage and frequency |
| poc_breaker | ElmCoup | FREQ, export (optional for FRT) — POC active/reactive power and current |
| gu_busbar | ElmTerm | FRT — ‘GU Terminal’ plot page |
| inverter | ElmGenstat or ElmSym | FRT, FRT export — representative generating unit |
| external_grid | ElmXnet | FRT, FREQ — fault level (Ssc, R/X) and voltage setpoint |
| station_ctrl | ElmStactrl | FRT, FREQ — Q setpoint |
| pfc_ctrl | ElmSecctrl | FRT, FREQ — P setpoint |
| freq_voltage_source | ElmVac | FREQ — frequency step events |

To list the element names in your model, run this in a PowerFactory Python console:

for cls in ["ElmTerm","ElmCoup","ElmXnet","ElmStactrl","ElmSecctrl","ElmVac","ElmGenstat"]:

for o in app.GetCalcRelevantObjects(f"*.{cls}"):

app.PrintPlain(f"{cls}: '{o.loc_name}'")

Grid code file:  the FRT script needs frt_scenarios (retained voltage levels and clearance times) and the frequency script needs simulation_timing and simulation_setup blocks. The NL Type D file in Working Scripts has these; the older copies in config/ do not yet.

# 4. Running FRT studies

## 4.1 Settings

| Setting (simulation:) | Meaning |
| --- | --- |
| setup_only | true (default): create the cases and fill Task Automation, run nothing. false: also run them. |
| run_sim_only | true: do not create cases — re-run the cases in the latest FRT_* run folder. |
| execution_mode | sequential (default): run each case from Python with full convergence checks. task_automation: run all cases as one Task Automation batch (can run in parallel). |
| fault_start_s, t_stop_s | Fault time and simulation end time [s] — required (the template uses 10 s and 20 s). |
| integration_step_s, t_start_s, a_stable_integration | RMS solver settings. |

## 4.2 Recommended workflow

- Set setup_only: true and run_sim_only: false, then execute the FRT ComPython object.

- Check the output window: the generated case list, the preflight checks (each element marked [ok]) and the new run folder FRT_<date>_<time> under Study Cases.

- Open one or two cases and check the fault events, setpoints and plot pages.

- Run the simulations — choose one option:

  - From the script (recommended): set setup_only: false and run_sim_only: true, then execute again. The latest run folder's cases are run and failures are recorded in the manifest.

  - From Task Automation: open Study Cases › Task Automation, set up the Parallel Computing page, press Execute. Faster, but the manifest will not record failures — check results by hand or re-run with the script.

To create and run in one go, set setup_only: false and run_sim_only: false.

## 4.3 What is created

- A study case per combination, named e.g. FRT 3PH 0.05 Q0, FRT 2PH 0.4 Qmax, FRT 1PH 0.85 Qmin, with a matching operation scenario holding its setpoints.

- Fault events at the POC: applied at fault_start_s, cleared after the grid code clearance time. The fault impedance is chosen to give the target retained voltage.

- Recorded variables at the POC and the inverter, and two plot pages: POC and GU Terminal.

- A run manifest FRT_<date>_<time>_manifest.json in output_dir, listing every case with its parameters and solved/failed status.

Note:  the fault impedance is a pre-fault estimate. The plant's reactive current raises the actual retained voltage, so compare achieved and target Uret in the results.

# 5. Running frequency studies

gcc_freq_script.py uses the same config file and the same setup_only / run_sim_only flags. Cases always run sequentially. Timing and step sequences come from the grid code file only.

- Set setup_only: true, run_sim_only: false and execute the frequency ComPython object.

- Check the run folder FREQ_<date>_<time>: a Ramp and a Step case for each applicable mode (FSM, LFSMO, LFSMU), each with three plot pages.

- Set setup_only: false, run_sim_only: true and execute again to run the cases.

Step events are created on the frequency source as <TYPE>_Step_<freq>Hz_t<time>s (e.g. LFSMO_Step_50.2Hz_t30s). Re-running replaces them, and other events in the base case are left alone.

Remember:  setup_only and run_sim_only are shared by both scripts. Set them to the step you want before running either one.

# 6. Exporting results

Run the exporter after the simulations have finished. It reads results only and changes nothing in the model.

- In gcc_export_results.py set STUDY = "FRT" or "FREQ".

- Leave RUN_TAG = None to pick the run from a dialog (Ctrl-click to export several runs at once), or set it to a folder name such as "FRT_2026-07-12_13-44-25".

- Execute the exporter ComPython object.

Output, inside output_dir:

FRT_2026-07-12_13-44-25\

FRT_3PH_0.05_Q0.csv

FRT_3PH_0.05_Qmax.csv

...

export_manifest.json

- Each CSV has a time_s column followed by one column per recorded variable (e.g. POC Pos-Seq Voltage [pu]).

- export_manifest.json maps every case to its CSV and carries all case parameters.

- Failed cases are skipped. Cases whose results stop before t_stop are exported with a warning.

Important:  the time step varies during a simulation, so rows are not evenly spaced. Always interpolate on time_s; never assume a fixed row interval.

## 6.1 Choosing an exporter

|  | gcc_export_results.py | gcc_export_results_Rev2.py |
| --- | --- | --- |
| Needs project config | Yes (CONFIG_FILE) | No — set OUTPUT_DIR in the script |
| Columns | Fixed list, friendly names | Everything recorded, “element ¦ variable” |
| Run manifest | Required | Optional (metadata missing without it) |

For Rev2, set OUTPUT_DIR to the same folder as results.output_dir so it finds the run manifests.

# 7. Troubleshooting

Every script checks its config, elements, base case and output folder before it creates anything, so an error at the start leaves the project untouched.

| Message or symptom | What to do |
| --- | --- |
| PyYAML is not installed | Install it (section 2.1) and restart PowerFactory. |
| Config file not found | Check CONFIG_FILE in the script and grid_code.file in the config. |
| Element not found — class: …, loc_name: … | Correct the name in the elements section (section 3). |
| Missing 'elements.…' / 'simulation.…' in project config | Add the missing key to the config. |
| Base case '…' not found | Create GCC_BaseCase or set elements.base_case. |
| Output folder is not writable | Fix results.output_dir. |
| No FRT study cases generated | The grid code block requirements_<plant_type>.fault_ride_through needs applicable: true, fault_types and frt_scenarios. |
| run_sim_only=True but no FRT_*/FREQ_* run folder | Run once with setup_only: true and run_sim_only: false first. |
| Run manifest not found (exporter) | The exporter looks in output_dir. Re-run the simulation script with setup_only: true and run_sim_only: true to rewrite it for the latest run folder. |
| Case FAILED — Initial conditions / did not complete / diverged | A model problem in that case. The other cases continue; the failed list in the summary can go to the OEM. |
| Script runs but prints nothing | Check that the ComPython object points at the script file itself. If it still does nothing, replace the last two lines of the script (if __name__ == "__main__": / main()) with a plain main(). |